Power PCB Relay      FTR-K3F Flat-Type relay

[FEATURES]

- Super Low profile (Height:18.2 mm)

- 25A rated current.(High capacity)

- High insulation in small package

# - Insulation distance		: 8mm min. (between coil and contacts)

- Dielectric strength		: 5,000VAC

- Surge strength			: 8,500V

- Plastic materials

- Flammability			: UL94  V-0

- UL,CSA,IEC

- UL				: Conform to UL508

- CSA				: Conform to CSA22.2 No.14

- VDE				: Conform to VDE 0435

- Features                                           : RoHS compliance (Lead free, Cd free)

[APPLICATIONS]

Heater controls, power supplies, air conditioning

- ORDERING INFORMATION

[EXAMPLE]   FTR-K3F   Ｊ    Ｂ    012    W

(a)        (b)     (c)    (d)    (e)

- Series Name			: FTR-K3F (FTR-K3 Flat and High capacity Type)

- Contact Arrangement	          A: Standard Type Ｊ : Faston-Terminal Type

- Coil Sensitive		          A : Standard Sensitive

- Coil Number			: Nominal Voltage

- Contact Material		           W: Silver Alloy  (AgSnO2)

- COIL DATA CHART

  - Chart 1

| Coil Number | Nominal Voltage [VDC] | Coil Resistance [ohms] (tolerance of 10% at 20 deg ) | Operate Voltage [VDC] (at 20 deg) | Release Voltage [VDC] (at 20 deg) | Nominal Power [mW] (tolerance of 10% at 20 deg) |
| --- | --- | --- | --- | --- | --- |
| 005 006 009 012 018 024 048 | 5 6 9 12 18 24 48 | 32 46 105 185 415 740 2,955 | 3.5 4.2 6.3 8.4 12.6 16.8 33.6 | 0.5 0.6 0.9 1.2 1.8 2.4 4.8 | 780 |

■SPECIFICATIONS

| Item | FTR-K3F High Capacity Type |
| --- | --- |
| Contact | Arrangement | 1 Form A |
|  | Material | Silver alloy (AgSnO2) |
|  | Resistance (initial) | Max. 100 m( (at 1A 6VDC) |
|  | Rating | 25A 250VAC |
|  | Max. Carrying Current | 25A |
|  | Max. Switching Power | 6250VA |
|  | Max. Switching Voltage | 250VAC |
|  | Min. Switching Load | 100mA 5VDC (Reference) |
|  | Max. Switching Current | 25A |
| Coil | Operating Temperature | -40 to +60 deg (no frost) |
| Time Value | Operate (without diode) | Max. 20ms (at nominal voltage, without bounce) |
|  | Release (without diode) | Max. 10ms (at nominal voltage, without bounce) |
| Insulation | Resistance (at 500VDC) | Min. 1000M( |
|  | Dielectric Strength | B/T contacts | 1000VAC, 1 minute |
|  |  | B/T coil and contacts | 5000VAC, 1 minute |
|  | Surge Strength | 8500V / 1.2x50(s |
| Life | Mechanical | 2 x 106 ope. min. |
|  | Electrical (Resistive load) | 100 x 103 ope. min. |
| Vibration Resistance | Miss operation | 10 to 55 Hz at double amplitude of 1.5mm |
|  | Endurance | 10 to 55 Hz at double amplitude of 1.5mm |
| Shock Resistance | Miss operation | Min. 100m/s2 (11(1ms) |
|  | Endurance | Min. 1000m/s2 (6(1ms) |
| Weight | Approx. 25g |

■DIMENSIONS (PCB-terminal TYPE)

# Text boxes

Under approval

■Schematics (Bottom View)

1st, Feb. 2006 Issue 3

- PC board mounting hole layout

(Bottom View)